1)Test Action (Test power trip):-

- Test all ‘3 pin plug socket’ at 2 rows with ‘ELCB & Socket tester’.

- 3 lights will show in ‘ELCB & Socket tester’.

- Turn ON ELCB switch RN2 & BN2 to run the test.

- Test power trip by press the red button.

- ELCB switch at RN2 will triggered and switch OFF.

- That’s mean ELCB switch is Ok.

- Incoming DB is still switch ON.

- No power trip at Incoming DB during this exercise.

2)Test Action (Check power load):-

- Plug power commando cable to rack.

- Turn ON ELCB switch RN2 & BN2.

- No power load in AMMETER (Blue/Yellow/Red) after plug in power commando to the power rack.

- That’s mean the rack has not used any power due to no equipment running on it.